## M2_Index
M2 PV Performance — INDEKS Famili Detektor
Peta tiap detektor → sinyal → fault_type → severity → status reproduksibilitas Excel. Workbook 45 detektor-sheet (di luar indeks ini). Detail: docs/M2_RE_0X_*.md + M2_Family_Summary.
1. Peta Detektor (9 aktif + 1 ML skeleton)
# | Detector | Modul | Sinyal utama | fault_type | Severity (ringkas) | Sheet keputusan | Status Excel
1 | M2eAvailability | availability.py | uptime inverter & string (downtime menit) | (severity-based) | <90 CRIT · <95 HIGH · <97 MED · <99 INFO · ≥99 NORMAL | M2e_Availability | PENUH
2 | M2bPeerZScore | peer_zscore.py | R_str=V/I → z-score peer + voc_ratio | high_R | ¦z¦>3.5 HIGH · ¦z¦>2.5 & voc_ratio>0.95 MED | M2b_PeerZScore | PENUH
3 | M2bOpenCircuit | open_circuit.py | I/I_q95 < 5% (across siblings) + debounce 20 | open_circuit | CRITICAL (conf 95%) | M2b_OpenCircuit | PENUH
4 | M2bGroundFault | ground_fault.py | V_to_ground absolute/adaptive + voc_ratio & I_z | ground_fault | spec+(abs¦adp)=90 · spec/abs+adp=80 · abs=70 · adp=60 | M2c_GroundFault | PENUH*
5 | M2bMpptRatio | mppt_ratio.py | I/median(partner se-MPPT) < 0.85 + debounce 20 | mppt_partner_underperform | rem<0.20 CRIT · <0.50 HIGH · else MED (conf 50–90) | M2b_MpptRatio | PENUH
6 | M2IForest | iforest.py | IsolationForest 5-fitur (V,I,V_dev,I_dev,R) | iforest_anomaly | kuartil rank flagged: CRIT/HIGH/MED/INFO | IF_Anomaly | APPROKSIMASI
7 | M2aLowIrradiance | m2a/low_irradiance.py | OLS slope PR_proxy vs POA (band low/mid) | low_irradiance / general_underperform | ¦slope_low¦·r² → CRIT/HIGH/MED | M2a_LowIrradiance | PENUH
8 | M2aShading | m2a/shading.py | CV antar-string per jam + PR + asimetri AM/PM | shading_morning/afternoon/uniform | 0.7·frac + 0.3·asym → CRIT/HIGH/MED | M2a_Shading | PENUH
9 | M2aSoiling | m2a/soiling.py (skeleton) | rdtools SRR (Monte-Carlo) → ekonomi payback | soiling_detected / cleaning_recommended / insufficient_data | (p_loss,payback) → CRIT/HIGH/MED/INFO | SO_Economics | HILIR PENUH
10 | M2bIntermittent (LSTM-AE) | lstm_ae.py (skeleton, enabled=False) | LSTM Autoencoder; reconstruction error window 24-jam (96×15-min) | intermittent | MEDIUM (conf 70) | (tak ada — input-only) | INPUT-ONLY
Legenda Status Excel
PENUH | Direproduksi eksak sebagai formula live (verified vs source, selisih ~0).
PENUH* | Per-inverter math live & eksak; SATU input representatif: fleet V_gnd median/std (ground_fault).
HILIR PENUH | Semua hilir live & eksak; satu nilai = INPUT black-box: soiling_ratio dari SRR Monte-Carlo.
APPROKSIMASI | Struktur faithful tapi SKOR proxy (MAD), BUKAN skor IsolationForest asli — menandai sampel berbeda.
INPUT-ONLY | Jaringan PyTorch terlatih = black box; TAK ADA sheet & tak ada lapisan hilir bermakna (LSTM-AE). Lihat M2_RE_10.
2. Inventaris Sheet & Dokumen (per iterasi)
Iterasi | Detector | Dokumen RE | Sheet
— | Inti (shared) | — | README, Config
2 | M2eAvailability | (Iterasi 2) | Raw_Data, EmptyPVMap, Helpers_M2e, M2e_Availability, M2e_AllStrings, Findings_Summary
3 | M2bPeerZScore | M2_RE_03 | PanelSpec, Raw_Data_M2b, Meteo_Dummy, Helpers_M2b, M2b_PeerZScore, M2b_StringStatus, M2b_StatComparison, Hampel_Preprocessing
4 | M2bOpenCircuit | M2_RE_04 | Raw_Data_OC, Helpers_OC, M2b_OpenCircuit, M2b_OC_StringStatus
5 | M2bGroundFault | M2_RE_05 | Raw_Data_GF, Helpers_GF, GF_StringMetrics, M2c_GroundFault, M2c_GF_StringStatus
6 | M2IForest | M2_RE_06 | Raw_Data_IF, Features_IF, IF_Anomaly, IF_Summary
7 | M2aLowIrradiance | M2_RE_07 | Raw_Data_LI, Helpers_LI, M2a_LowIrradiance, LI_Summary
8 | M2aShading | M2_RE_08 | Raw_Data_SH, Helpers_SH, SH_Hourly, M2a_Shading
9 | M2aSoiling | M2_RE_09 | Raw_Data_SO, Helpers_SO, SO_Economics, SO_Summary
10 | M2bIntermittent (LSTM-AE) | M2_RE_10 | (tak ada sheet — input-only; jaringan PyTorch terlatih)
11 | M2bMpptRatio | M2_RE_11 | Raw_Data_MR, Helpers_MR, M2b_MpptRatio, M2b_MR_StringStatus

## README
M2 PV Performance — Workbook Excel
Reverse engineering dari pv_pipeline/ (notebook 20260514stringmap_v1.5.ipynb)
Iterasi log
Iterasi | Tanggal | Detector | Sheet yang ditambah
1 (Phase 1) | 2026-05-28 | — | Hanya dokumen overview (.docx + .md). Belum ada Excel.
2 | 2026-05-28 | M2eAvailability | README, Config, Raw_Data, EmptyPVMap, Helpers_M2e, M2e_Availability, M2e_AllStrings, Findings_Summary
3 | 2026-05-28 | M2bPeerZScore | Meteo_Dummy, PanelSpec, Raw_Data_M2b, Helpers_M2b, M2b_PeerZScore, M2b_StringStatus, Hampel_Preprocessing, M2b_StatComparison
4 | 2026-05-29 | M2bOpenCircuit | Raw_Data_OC, Helpers_OC, M2b_OpenCircuit, M2b_OC_StringStatus
5 | 2026-05-30 | M2bGroundFault | Raw_Data_GF, Helpers_GF, GF_StringMetrics, M2c_GroundFault, M2c_GF_StringStatus
6 | 2026-05-30 | M2IForest (approx) | Raw_Data_IF, Features_IF, IF_Anomaly, IF_Summary [APPROKSIMASI MAD — bukan true iForest]
7 | 2026-05-30 | M2aLowIrradiance | Raw_Data_LI, Helpers_LI, M2a_LowIrradiance, LI_Summary (dibangun ulang 2026-09-28: relatif-tetangga)
8 | 2026-05-30 | M2aShading | Raw_Data_SH, Helpers_SH, SH_Hourly, M2a_Shading
9 | 2026-05-30 | M2aSoiling (skeleton) | Raw_Data_SO, Helpers_SO, SO_Economics, SO_Summary [SRR=input, ekonomi=live]
11 | 2026-06-13 | M2bMpptRatio | Raw_Data_MR, Helpers_MR, M2b_MpptRatio, M2b_MR_StringStatus
Cara membaca
• Sheet 'Config' adalah single source of truth untuk semua threshold. Edit di sini → seluruh workbook recalc.
• Sheet 'Raw_Data' berisi data dummy realistis. Ganti dengan data aktual mu (paste over) untuk pakai workbook ini di lapangan.
• Sheet 'Helpers_M2e' adalah JEMBATAN antara Raw_Data dan M2e_Availability. Tiap kolom punya formula yang ekuivalen dengan satu langkah di pv_pipeline/availability.py.
• Sheet 'M2e_Availability' menampilkan hasil akhir per inverter & per string + severity. Sheet 'M2e_AllStrings' mereplika output sheet xlsx Python.
• Severity dihitung via IFS() dari uptime_pct ke threshold di Config.
• Workbook ini akan TUMBUH per iterasi — sheet baru ditambah tanpa mengubah yang lama.

## Config
M2 Configuration (mirror config/m2_config.yaml)
Section | Key | Value | Unit / Notes
m2e.severity | critical_below | 90 | % uptime; < ini → CRITICAL
m2e.severity | high_below | 95 | % uptime; < ini → HIGH
m2e.severity | medium_below | 97 | % uptime; < ini → MEDIUM
m2e.severity | info_below | 99 | % uptime; < ini → INFO; ≥ ini → NORMAL
m2e.severity | emit_normal | 0 | 1=emit NORMAL findings, 0=skip
m2e.string_proxy | pstr_zero_threshold_kw | 0.1 | kW; PV power < ini → string dianggap mati
m2e.string_proxy | sibling_median_active_kw | 1 | kW; median sibling >= ini → timestamp 'produktif'
m2e.string_proxy | min_active_siblings_pct | 50 | %; minimum % sibling aktif → 'qualified' timestamp
m2e.string_proxy | debounce_consecutive_steps | 2 | step; run candidate >= ini → genuine event. DUMMY=2 (original spec). PRODUKSI IKN=20 (~1h40m persist).
system | interval_minutes | 5 | menit; median selisih Start Time (auto-detected, override saat dummy)
system | pv_max | 28 | PV string per inverter (hardcoded Huawei cap)
system | n_pv_total_in_workbook | 5 | PV string yang ada di sheet ini (PV1..PV5)
m2b | poa_threshold_wm2 | 300 | W/m²; ¦z¦ Z-score hanya hitung saat POA > ini (spec 4.2.1)
m2b | poa_floor_wm2 | 50 | W/m²; sunset fix — POA harus > ini (sensor lag protection)
m2b | z_threshold | 2.5 | ¦z¦ > ini → flag suspect (spec 4.2.1)
m2b | z_high_threshold | 3.5 | ¦z¦ > ini → severity HIGH; else MEDIUM
m2b | voc_ratio_threshold | 0.95 | voc_actual/voc_string_nominal > ini → confirm high_R (spec 4.2.3)
m2b | stat_method | median | mean ¦ median ¦ both (z_primary picker)
m2b | min_peer_strings | 3 | min sibling per inverter untuk valid peer comparison
m2b | min_daylight_samples | 10 | min samples lulus POA gate per inverter
m2b | i_clip_floor_a | 0.1 | clip(lower=0.1A) untuk hindari divide-by-zero saat R=V/I
voc_estimator | i_threshold_a | 0.5 | I < ini → dianggap open-circuit (sunrise/sunset)
voc_estimator | min_voc_v | 10 | V > ini → buang zero-reading sample
voc_estimator | min_samples | 3 | minimum samples valid untuk median voc
preprocessing | hampel_window | 15 | samples; rolling window (75 menit @ 5-min)
preprocessing | hampel_max_deviation | 3 | MAD-sigma; ¦x - median¦ / MAD > ini → outlier
preprocessing | enabled | 0 | 1=apply Hampel cleaning, 0=skip (raw V/I)
poa | default_source | pyranometer_avg | single source di dummy (production: 5 sources)
m2b_open_circuit | poa_threshold_wm2 | 700 | W/m²; daylight gate utama (config override; spec 4.2.3 tulis 200)
m2b_open_circuit | poa_floor_wm2 | 50 | W/m²; hard floor sunset/twilight (sensor-lag protection)
m2b_open_circuit | i_ratio_threshold | 0.05 | I_string/I_q95 < ini → qualifying (spec 4.2.3: <5%)
m2b_open_circuit | debounce_consecutive_steps | 20 | qualifying harus ≥N step konsekutif → genuine event (~100min @5-min)
m2b_open_circuit | confidence_pct | 95 | confidence finding (spec 4.2.3)
m2b_open_circuit | iq95_clip_floor_a | 0.01 | clip(lower) I_q95 untuk hindari div-by-zero
m2b_ground_fault | poa_threshold_wm2 | 200 | W/m²; daylight gate (selaras spec 4.2.3 & default kode)
m2b_ground_fault | poa_floor_wm2 | 50 | W/m²; hard floor sunset/twilight
m2b_ground_fault | v_to_ground_abs_threshold_v | 50 | MAX¦V_PV-ground¦ > ini → trigger 'absolute'
m2b_ground_fault | adaptive_z_threshold | 3 | ¦median-fleet¦/std > ini → trigger 'adaptive'
m2b_ground_fault | voc_ratio_threshold | 0.85 | voc_ratio < ini (+i_z>2) → trigger 'spec_4.2.3'
m2b_ground_fault | i_high_z_threshold | 2 | peer I z-score > ini → arus abnormal tinggi (spec)
m2b_ground_fault | fleet_v_gnd_median_v | 0 | INPUT: median V_gnd fleet (~200 inv IKN); demo tak reproduksi fleet penuh
m2b_ground_fault | fleet_v_gnd_std_v | 8 | INPUT: std V_gnd fleet; lihat catatan limitasi §5
m2_iforest | contamination_demo | 0.05 | fraksi anomali demo (default produksi 0.01)
m2_iforest | r_current_floor_a | 0.1 | R = V / MAX(I, ini) (proxy resistansi)
m2_iforest | mad_scale | 1.4826 | MAD → sigma (konsistensi normal): z = ¦x-med¦/(1.4826·MAD)
m2_iforest | real_contamination | 0.01 | DOKUMENTASI: contamination iForest asli (sklearn)
m2_iforest | real_n_estimators | 100 | DOKUMENTASI: n_estimators iForest asli
m2_iforest | real_random_state | 42 | DOKUMENTASI: random_state iForest asli (reproducible)
m2a_low_irradiance | poa_low_min | 50 | band low POA min (W/m²)
m2a_low_irradiance | poa_low_max | 250 | band low POA max
m2a_low_irradiance | poa_mid_min | 300 | band mid POA min (cross-check soiling)
m2a_low_irradiance | poa_mid_max | 800 | band mid POA max
m2a_low_irradiance | low_ratio_threshold | 0.9 | low_ratio < ini -> kandidat flag (relatif median tetangga se-WB)
m2a_low_irradiance | robust_z_min | 3 | ...DAN robust-z < -nilai ini terhadap inverter se-WB-hari
m2a_low_irradiance | min_low_samples | 12 | min sampel pita rendah bermatahari tinggi (1 jam @5 menit)
m2a_shading | poa_threshold_wm2 | 100 | gate daylight (W/m²)
m2a_shading | cv_low_multiplier | 0.5 | cv_hour < ini·median(cv) → CV rendah (uniform)
m2a_shading | pr_low_multiplier | 0.85 | pr_hour < ini·median(pr) → underperform
m2a_shading | am_pm_split_hour | 12 | batas AM/PM untuk asimetri diurnal
m2a_shading | asymmetry_threshold | 0.5 | asimetri < ini → uniform (soiling/awan), bukan terrain
m2a_shading | min_hours_for_analysis | 4 | min jam untuk median referensi
m2a_shading | min_samples_per_hour | 5 | min sampel (PV×ts) per jam
m2a_soiling | min_days | 90 | min window hari untuk SRR (skeleton gate)
m2a_soiling | capacity_kwp | 71500 | kapasitas DC site PLTS-IKN (PR denominator)
m2a_soiling | electricity_tariff_idr | 1500 | tarif PPA (IDR/kWh)
m2a_soiling | cleaning_cost_idr | 50000000 | biaya 1 cleaning (DEMO; default 0 = user wajib isi)
m2a_soiling | payback_threshold_days | 30 | payback < ini → recommend cleaning
m2b_mppt_ratio | poa_threshold_wm2 | 300 | moderate sun gate
m2b_mppt_ratio | poa_floor_wm2 | 50 | hard floor twilight
m2b_mppt_ratio | ratio_threshold | 0.85 | I<85% median partner -> qualifying
m2b_mppt_ratio | ratio_high | 0.5 | event_median<0.50 -> HIGH
m2b_mppt_ratio | ratio_critical | 0.2 | event_median<0.20 -> CRITICAL
m2b_mppt_ratio | debounce_consecutive_steps | 20 | ~100 menit @ 5-min
m2b_mppt_ratio | min_partner_strings | 1 | grup 2-string tetap dianalisis
m2b_mppt_ratio | partner_clip | 0.01 | clip(lower=0.01) divide-by-zero guard
m2a_low_irradiance | low_band_min_elevation_deg | 30 | pita rendah hanya saat matahari >= ini (awan siang, bukan matahari rendah)
m2a_low_irradiance | min_peers | 5 | min inverter se-WB per timestamp untuk median tetangga
m2a_low_irradiance | min_mid_samples | 30 | min sampel pita menengah (normalisasi e)

## Raw_Data
Raw_Data (dummy realistis — 2 inverter × 12 timestep)
Skenario: INV01 punya PV3 fault 6-timestep; INV02 down 4-timestep. PV5 (kedua inverter) ada di EmptyPVMap.
Inverter_ID | Start Time | Inverter status | PV1 Power(kW) | PV2 Power(kW) | PV3 Power(kW) | PV4 Power(kW) | PV5 Power(kW)
WB02-INV01 | 2026-05-14 10:00 | Grid connected | 5 | 4.9 | 5.1 | 5 | 0
WB02-INV01 | 2026-05-14 10:05 | Grid connected | 5.05 | 4.94 | 5.1 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:10 | Grid connected | 5.1 | 4.98 | 5.1 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:15 | Grid connected | 5.15 | 5.02 | 0 | 5 | 0
WB02-INV01 | 2026-05-14 10:20 | Grid connected | 5 | 5.06 | 0 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:25 | Grid connected | 5.05 | 4.9 | 0 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:30 | Grid connected | 5.1 | 4.94 | 0 | 5 | 0
WB02-INV01 | 2026-05-14 10:35 | Grid connected | 5.15 | 4.98 | 0 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:40 | Grid connected | 5 | 5.02 | 0 | 5.06 | 0
WB02-INV01 | 2026-05-14 10:45 | Grid connected | 5.05 | 5.06 | 5.1 | 5 | 0
WB02-INV01 | 2026-05-14 10:50 | Grid connected | 5.1 | 4.9 | 5.1 | 5.03 | 0
WB02-INV01 | 2026-05-14 10:55 | Grid connected | 5.15 | 4.94 | 5.1 | 5.06 | 0
WB02-INV02 | 2026-05-14 10:00 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:05 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:10 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:15 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:20 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:25 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:30 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:35 | Shutdown command | 0 | 0 | 0 | 0 | 0
WB02-INV02 | 2026-05-14 10:40 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:45 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:50 | Grid connected | 5 | 5 | 5 | 5 | 0
WB02-INV02 | 2026-05-14 10:55 | Grid connected | 5 | 5 | 5 | 5 | 0

## EmptyPVMap
EmptyPVMap — slot PV yang fisik tidak terpasang (skip dari peer comparison)
Replica config/strings.yaml (245 inverter dalam file aktual). Di sini hanya entry yang relevan untuk dummy.
Inverter_ID | Empty PV indices (CSV) | Note
WB02-INV01 | 5 | DEMO: PV5 EMPTY by design
WB02-INV02 | 5 | DEMO: PV5 EMPTY by design
WB01-INV01 | 19,20,21,22,23,24,25,26,27,28 | Pola WB01 produksi (PV19-28 kosong)
WB03-INV01 |  | (contoh: tidak ada slot kosong)
WB05-INV05 | 5 | DEMO M2b: PV5 EMPTY

## Helpers_M2e
Helpers_M2e — derived columns dari Raw_Data (per-row formulas)
Setiap kolom = 1 langkah di pv_pipeline/availability.py. Edit Raw_Data → recalc otomatis.
Inverter_ID | Start Time | status_raw | _status_class | sib_median_kW | active_count | active_pct | qualified | is_on | cand_PV1 | run_id_PV1 | run_len_PV1 | in_event_PV1 | cand_PV2 | run_id_PV2 | run_len_PV2 | in_event_PV2 | cand_PV3 | run_id_PV3 | run_len_PV3 | in_event_PV3 | cand_PV4 | run_id_PV4 | run_len_PV4 | in_event_PV4 | cand_PV5 | run_id_PV5 | run_len_PV5 | in_event_PV5

## M2e_Availability
M2e Availability — output finding per inverter & per string
Section A: per-inverter uptime%. Section B: per-string proxy down. Severity di-derive dari uptime_pct vs threshold di Config.
A. Per-inverter daily uptime
Inverter_ID | n_on | n_down | denom | uptime_pct | downtime_min | severity | threshold_breached | message
WB02-INV01
WB02-INV02
B. Per-string proxy down (event_minutes_total + uptime_pct + severity)
Inverter_ID | PV_string | daylight_minutes_inv | event_minutes | n_events | string_uptime_pct | severity | is_empty | message
WB02-INV01 | PV1
WB02-INV01 | PV2
WB02-INV01 | PV3
WB02-INV01 | PV4
WB02-INV01 | PV5
WB02-INV02 | PV1
WB02-INV02 | PV2
WB02-INV02 | PV3
WB02-INV02 | PV4
WB02-INV02 | PV5

## M2e_AllStrings
M2e_AllStrings — tabel rapi per (inverter × PV string) — replika output Python
Setiap baris = 1 PV slot. status ∈ {EMPTY, NO_DAYLIGHT, NORMAL, INFO, MEDIUM, HIGH, CRITICAL}. Pull dari M2e_Availability Section B.
inverter_id | pv_string | status | uptime_pct | downtime_minutes | event_minutes | n_events | daylight_minutes

## Findings_Summary
Findings_Summary — agregat semua finding NON-NORMAL & NON-EMPTY
Saat ini hanya M2e. Akan tumbuh: M2b, M2a, IsolationForest, dst. Setiap iterasi tambah sheet detector → tambah baris di sini.
Source Sheet | sub_module | inverter_id | pv_string | severity | value (uptime_pct) | threshold | message
M2e_Availability!A (inverter) | M2e_inverter
M2e_Availability!A (inverter) | M2e_inverter
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
M2e_Availability!B (string proxy) | M2e_string_proxy |  |  |  |  | (see Config)
--- M2b PeerZScore ---
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV1
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV2
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV3
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV4
M2b_PeerZScore!C | M2b_peer_zscore | WB05-INV05 | PV5 | EMPTY | - | - | -

## PanelSpec
PanelSpec — Jinko JKM625N 78HL4-BDV (mirror config/panel_spec.yaml)
Konsumen: PanelSpec.voc_at_cell_temp + voc_string_nominal di peer_zscore.py
Parameter | Value | Unit | Notes
panel_model | Jinko JKM625N 78HL4-BDV |  | Bifacial Tiger Neo dual-glass
voc_stc_v | 55.72 | V | Open-circuit voltage @ STC (1000 W/m², 25°C cell)
vmp_stc_v | 46.1 | V | Max-power voltage @ STC
imp_stc_a | 13.56 | A | Max-power current @ STC
isc_stc_a | 14.27 | A | Short-circuit current @ STC
pmax_stc_w | 625 | W | Max power @ STC
voc_noct_v | 52.93 | V | Voc @ NOCT (800 W/m², 20°C ambient)
temp_coef_voc_pct_per_c | -0.25 | %/°C | Voc decreases when Tcell rises
temp_coef_pmax_pct_per_c | -0.29 | %/°C | Pmax temperature coefficient
temp_coef_isc_pct_per_c | 0.045 | %/°C | Isc temperature coefficient (small +)
t_stc_c | 25 | °C | STC reference temperature
max_system_voltage_v | 1500 | V | IEC limit
default_modules_per_string | 26 | modules | Fallback (WB03-10)
modules_per_string_WB01 | 24 | modules | PLTS-IKN WB01 layout
modules_per_string_WB02 | 24 | modules | PLTS-IKN WB02 layout
modules_per_string_WB03_10 | 26 | modules | PLTS-IKN WB03-10 layout
voc_at_cell_temp(T_cell) — Excel formula
Input: cell_temp_c → | 30 | °C (edit untuk recalc)
voc_per_module = voc_stc × (1 + temp_coef_voc/100 × (T - 25)) |  | V per modul
voc_string_WB01_WB02 (24 modules) |  | V per string (cold Voc skenario)
voc_string_WB03_WB10 (26 modules) |  | V per string

## Raw_Data_M2b
Raw_Data_M2b — extended dummy data (WB05-INV05, 24 timestep)
Skenario: 06:00-06:55 sunrise (I≈0, V≈Voc), 12:00-13:55 noon (full sun). PV3 punya HIGH-R fault (I drop 60%, V naik sedikit) → expected flag.
Inverter_ID | Start Time | Inverter status | PV1 input voltage(V) | PV1 input current(A) | PV2 input voltage(V) | PV2 input current(A) | PV3 input voltage(V) | PV3 input current(A) | PV4 input voltage(V) | PV4 input current(A) | PV5 input voltage(V) | PV5 input current(A)
WB05-INV05 | 2026-05-14 06:00 | Grid connected | 1467.49 | -0.023 | 1469.34 | 0.023 | 1469.96 | -0.036 | 1468.08 | -0.042 | 0 | 0
WB05-INV05 | 2026-05-14 06:05 | Grid connected | 1462.29 | 0.071 | 1464.79 | 0.106 | 1463.07 | 0.11 | 1465.42 | 0.052 | 0 | 0
WB05-INV05 | 2026-05-14 06:10 | Grid connected | 1469.42 | 0.105 | 1471.89 | 0.123 | 1468.43 | 0.099 | 1471.45 | 0.15 | 0 | 0
WB05-INV05 | 2026-05-14 06:15 | Grid connected | 1470.22 | 0.193 | 1469.59 | 0.151 | 1471.39 | 0.158 | 1471.52 | 0.154 | 0 | 0
WB05-INV05 | 2026-05-14 06:20 | Grid connected | 1467.96 | -0.012 | 1467.36 | -0.018 | 1467.45 | -0.013 | 1469.59 | -0.004 | 0 | 0
WB05-INV05 | 2026-05-14 06:25 | Grid connected | 1464.77 | 0.086 | 1466.29 | 0.053 | 1464.39 | 0.065 | 1464.36 | 0.03 | 0 | 0
WB05-INV05 | 2026-05-14 06:30 | Grid connected | 1472.12 | 0.146 | 1473.27 | 0.156 | 1470.81 | 0.081 | 1471.16 | 0.105 | 0 | 0
WB05-INV05 | 2026-05-14 06:35 | Grid connected | 1465.62 | 0.17 | 1464.73 | 0.178 | 1465.77 | 0.184 | 1463.17 | 0.163 | 0 | 0
WB05-INV05 | 2026-05-14 06:40 | Grid connected | 1467.95 | 0.092 | 1467.21 | 0.024 | 1469.6 | 0.054 | 1465.98 | 0.007 | 0 | 0
WB05-INV05 | 2026-05-14 06:45 | Grid connected | 1464.26 | 0.118 | 1461.35 | 0.114 | 1465.08 | 0.128 | 1464.98 | 0.162 | 0 | 0
WB05-INV05 | 2026-05-14 06:50 | Grid connected | 1462.84 | 0.148 | 1461.18 | 0.158 | 1460.56 | 0.138 | 1461.93 | 0.19 | 0 | 0
WB05-INV05 | 2026-05-14 06:55 | Grid connected | 1470.76 | 0.021 | 1472.41 | 0.09 | 1469.95 | 0.067 | 1471.19 | 0.018 | 0 | 0
WB05-INV05 | 2026-05-14 12:00 | Grid connected | 1205.31 | 13.015 | 1202.2 | 12.994 | 1238.4 | 5.248 | 1205.72 | 13.045 | 0 | 0
WB05-INV05 | 2026-05-14 12:05 | Grid connected | 1198.43 | 12.912 | 1195.26 | 12.866 | 1231.1 | 5.173 | 1197.98 | 12.83 | 0 | 0
WB05-INV05 | 2026-05-14 12:10 | Grid connected | 1198.66 | 13.052 | 1199.3 | 12.986 | 1235.75 | 5.229 | 1198.41 | 12.996 | 0 | 0
WB05-INV05 | 2026-05-14 12:15 | Grid connected | 1207.67 | 13.047 | 1206.41 | 13.017 | 1243.51 | 5.227 | 1206.84 | 13.017 | 0 | 0
WB05-INV05 | 2026-05-14 12:20 | Grid connected | 1192.05 | 13.08 | 1194.57 | 12.996 | 1227.88 | 5.233 | 1191.99 | 13.003 | 0 | 0
WB05-INV05 | 2026-05-14 12:25 | Grid connected | 1206.86 | 13.05 | 1208.2 | 12.99 | 1241.56 | 5.202 | 1206.66 | 13.018 | 0 | 0
WB05-INV05 | 2026-05-14 12:30 | Grid connected | 1205.6 | 13.012 | 1203.28 | 13.036 | 1241.22 | 5.196 | 1202.43 | 13.047 | 0 | 0
WB05-INV05 | 2026-05-14 12:35 | Grid connected | 1197.75 | 12.976 | 1198.52 | 12.97 | 1234.91 | 5.128 | 1200.75 | 12.967 | 0 | 0
WB05-INV05 | 2026-05-14 12:40 | Grid connected | 1208.9 | 13.095 | 1207.45 | 13.099 | 1243.33 | 5.207 | 1207.02 | 13.176 | 0 | 0
WB05-INV05 | 2026-05-14 12:45 | Grid connected | 1196.06 | 13.078 | 1198.07 | 13.135 | 1232.35 | 5.256 | 1194.86 | 13.065 | 0 | 0
WB05-INV05 | 2026-05-14 12:50 | Grid connected | 1207.67 | 13.049 | 1205.73 | 13.032 | 1243.74 | 5.245 | 1206.13 | 13.07 | 0 | 0
WB05-INV05 | 2026-05-14 12:55 | Grid connected | 1193.66 | 12.923 | 1192.22 | 12.868 | 1230.64 | 5.137 | 1193.66 | 12.918 | 0 | 0

## Meteo_Dummy
Meteo_Dummy — POA (Plane-of-Array) per timestamp
Single source 'pyranometer_avg' (dummy). Produksi: 5 source fan-out (pyranometer_per_ws, pyranometer_avg, pvlib_clearsky_ineichen/simplified_solis/haurwitz).
Start Time | POA pyranometer_avg (W/m²) | Notes
2026-05-14 06:00 | 30 | sunrise (below gate)
2026-05-14 06:05 | 34.5 | sunrise (below gate)
2026-05-14 06:10 | 39.1 | sunrise (below gate)
2026-05-14 06:15 | 43.6 | sunrise (below gate)
2026-05-14 06:20 | 48.2 | sunrise (below gate)
2026-05-14 06:25 | 52.7 | sunrise (below gate)
2026-05-14 06:30 | 57.3 | sunrise (below gate)
2026-05-14 06:35 | 61.8 | sunrise (below gate)
2026-05-14 06:40 | 66.4 | sunrise (below gate)
2026-05-14 06:45 | 70.9 | sunrise (below gate)
2026-05-14 06:50 | 75.5 | sunrise (below gate)
2026-05-14 06:55 | 80 | sunrise (below gate)
2026-05-14 12:00 | 847.6 | noon (above gate)
2026-05-14 12:05 | 857.5 | noon (above gate)
2026-05-14 12:10 | 860.7 | noon (above gate)
2026-05-14 12:15 | 878 | noon (above gate)
2026-05-14 12:20 | 861.1 | noon (above gate)
2026-05-14 12:25 | 881.5 | noon (above gate)
2026-05-14 12:30 | 872.2 | noon (above gate)
2026-05-14 12:35 | 881.9 | noon (above gate)
2026-05-14 12:40 | 895.2 | noon (above gate)
2026-05-14 12:45 | 889 | noon (above gate)
2026-05-14 12:50 | 894.5 | noon (above gate)
2026-05-14 12:55 | 912.6 | noon (above gate)

## Helpers_M2b
Helpers_M2b — derived columns per row dari Raw_Data_M2b
Per-row: POA value (VLOOKUP dari Meteo_Dummy), mask_poa, R_str per PV. Aggregate (R_str median per PV, fleet stats) ada di sheet M2b_PeerZScore.
Inverter_ID | Start Time | status | POA_Wm2 | mask_poa | is_on | PV1_V | PV1_I | PV1_R | PV1_voc_cand | PV2_V | PV2_I | PV2_R | PV2_voc_cand | PV3_V | PV3_I | PV3_R | PV3_voc_cand | PV4_V | PV4_I | PV4_R | PV4_voc_cand | PV5_V | PV5_I | PV5_R | PV5_voc_cand

## M2b_PeerZScore
M2b PeerZScore — agregat per PV (R_str median dari mask_poa samples) + Z-score + voc_ratio + fault decision
Spec 4.2.1: ¦z¦ > 2.5 → flag. Spec 4.2.3 high_R: AND voc_ratio > 0.95 → emit. Confidence = min(90, ¦z¦/4*100). Severity: ¦z¦ > 3.5 HIGH else MEDIUM.
A. Per-PV string metrics (WB05-INV05, 5 PV strings)
PV_string | R_str (median) | voc_actual_v (median I<0.5A) | voc_string_nominal_v | voc_ratio | n_R_samples | n_voc_samples
PV1
PV2
PV3
PV4
PV5
B. Fleet statistics across PV1..PV5 (skip blanks)
Metric | Value
R_str fleet mean
R_str fleet median
R_str fleet std (sample stdev)
C. Z-score & fault decision per PV
PV_string | z_mean | z_median | z_primary (per stat_method) | flagged_by_z (¦z¦>2.5) | voc_ok (voc_ratio>0.95) | emit_finding | fault_type | severity | confidence_pct | message
PV1
PV2
PV3
PV4
PV5

## M2b_StringStatus
M2b_StringStatus — replika Python self.artifacts['StringStatus']
Pull dari M2b_PeerZScore sections A & C.
poa_source | inverter_id | wb_id | pv_string | status | rstr | rstr_fleet_median | rstr_fleet_std | z_mean | z_median | voc_actual_v | voc_string_nominal_v | voc_ratio | voc_ok | emitted_finding
pyranometer_avg | WB05-INV05 | WB05 | PV1
pyranometer_avg | WB05-INV05 | WB05 | PV2
pyranometer_avg | WB05-INV05 | WB05 | PV3
pyranometer_avg | WB05-INV05 | WB05 | PV4
pyranometer_avg | WB05-INV05 | WB05 | PV5 | EMPTY

## M2b_StatComparison
M2b StatComparison — Z-score mean vs median cross-check
Spec dual-stat: ¦z_mean¦ dan ¦z_median¦ dievaluasi. flagged_by_mean / flagged_by_median. Median lebih robust ke outlier (PV3 fault tidak skew median sebanyak mean).
PV_string | R_str | z_mean (vs fleet_mean) | z_median (vs fleet_median) | ¦z_mean¦ > 2.5? | ¦z_median¦ > 2.5? | agree (both flagged)? | diff ¦z_mean - z_median¦
PV1
PV2
PV3
PV4
PV5

## Hampel_Preprocessing
Hampel Preprocessing — A/B comparison V series original vs Hampel-cleaned
Demo Wave 9: rolling median window 15 (75-min) + MAD-based outlier mask. Approximation of pvanalytics.quality.outliers.hampel(). Toggle via cfg_enabled.
Note: rolling_MAD pakai AVEDEV (mean-abs-dev) = proxy MAD universal-compatible (MEDIAN(IF()) array gagal tanpa CSE di LibreOffice). True Hampel = median-abs-dev x 1.4826; AVEDEV strict ~1.2533. Demo mekanisme, bukan filter produksi (preprocessing.py pakai pvanalytics).
Start Time | PV3_V_original | rolling_median (window 15) | abs_dev_from_median | rolling_MAD | deviation_in_MAD_sigma | is_outlier | PV3_V_cleaned

## Raw_Data_OC
Raw_Data_OC — time-series arus per PV string (WB05-INV05)
Dummy 1 inverter, 5 PV string. PV1/PV2 healthy · PV3 GENUINE open-circuit · PV4 glitch 3-step · PV5 EMPTY.
24 baris daylight (12:00–13:55 @5-min, POA=900) + 2 baris twilight (18:10/18:20, POA=120 → gated). Ganti dengan data Huawei aktual (paste over).
Start Time | POA (W/m²) | PV1 input current(A) | PV2 input current(A) | PV3 input current(A) | PV4 input current(A) | PV5 input current(A)
2026-05-14 12:00 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:05 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:10 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:15 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:20 | 900 | 13 | 12.8 | 0.1 | 0.05 | 0
2026-05-14 12:25 | 900 | 13 | 12.8 | 0.1 | 0.05 | 0
2026-05-14 12:30 | 900 | 13 | 12.8 | 0.1 | 0.05 | 0
2026-05-14 12:35 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:40 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:45 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:50 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 12:55 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:00 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:05 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:10 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:15 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:20 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:25 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:30 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:35 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:40 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:45 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:50 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 13:55 | 900 | 13 | 12.8 | 0.1 | 12.9 | 0
2026-05-14 18:10 | 120 | 0 | 0 | 0 | 0 | 0
2026-05-14 18:20 | 120 | 0 | 0 | 0 | 0 | 0

## Helpers_OC
Helpers_OC — jembatan open_circuit.py (per-row mekanik)
I_q95 = PERCENTILE(arus PV1..PV5 baris itu, 0.95) ≡ quantile(0.95,axis=1). ratio = I/MAX(I_q95,0.01). qualifying = (ratio<thr) DAN daylight.
consec = running counter qualifying konsekutif (reset saat gagal). emit <=> MAX(consec) ≥ debounce. Production juga AND solar_elev>5° & inverter-shutdown (ephemeris, tak direplika statis).
Start Time | POA | daylight | I_q95 | ratio PV1 | ratio PV2 | ratio PV3 | ratio PV4 | ratio PV5 | qual PV1 | qual PV2 | qual PV3 | qual PV4 | qual PV5 | consec PV1 | consec PV2 | consec PV3 | consec PV4 | consec PV5

## M2b_OpenCircuit
M2b_OpenCircuit — keputusan per-PV (open_circuit.py run())
emit = (MAX consec ≥ debounce) DAN bukan EMPTY. ratio_median/I_median = MEDIAN over baris daylight (rows 5..28, blok kontigu).
PV3 sustained → run=24 ≥ 20 → CRITICAL conf 95%. PV4 glitch run=3 < 20 → suppressed. PV5 EMPTY → skip (q95 ikut 0-nya, harmless).
PV | I_median (daylight) | I_q95_median (daylight) | ratio_median (daylight) | MAX consec | empty_by_design | emit | status | severity | confidence | message
PV1 |  |  |  |  | 0
PV2 |  |  |  |  | 0
PV3 |  |  |  |  | 0
PV4 |  |  |  |  | 0
PV5 |  |  |  |  | 1

## M2b_OC_StringStatus
M2b_OC_StringStatus — replika artifact StringStatus (open_circuit.py)
Mirror self.artifacts['StringStatus']: per-PV status + median stats + debounce counts. EMPTY rows dari top-up EmptyPVMap.
poa_source | inverter_id | wb_id | pv_string | status | i_string_median_daylight | i_q95_median_daylight | ratio_median_daylight | n_qualifying_steps | n_debounced_events | emitted_finding | daylight_samples
dummy_single | WB05-INV05 | WB05 | PV1
dummy_single | WB05-INV05 | WB05 | PV2
dummy_single | WB05-INV05 | WB05 | PV3
dummy_single | WB05-INV05 | WB05 | PV4
dummy_single | WB05-INV05 | WB05 | PV5

## Raw_Data_GF
Raw_Data_GF — V/I per PV string + V_to_ground (4 inverter WB05)
INV01 NORMAL · INV02 V_to_ground tinggi (abs+adaptive) · INV03 PV3 ground-fault (spec: Voc↓ + I↑) · INV04 V_gnd tinggi + PV3 spec.
Tiap inverter: 3 baris dawn (06:00-06:10, I≈0 → Voc estimate) + 6 baris noon (12:00-12:25, POA=900 daylight). Empty slot PV5 (INV01/02) = 0.
Start Time | Inverter_ID | POA (W/m²) | V_to_ground (V) | PV1 input voltage(V) | PV2 input voltage(V) | PV3 input voltage(V) | PV4 input voltage(V) | PV5 input voltage(V) | PV6 input voltage(V) | PV1 input current(A) | PV2 input current(A) | PV3 input current(A) | PV4 input current(A) | PV5 input current(A) | PV6 input current(A)
2026-05-14 06:00 | WB05-INV01 | 100 | 2 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 06:05 | WB05-INV01 | 100 | 2 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 06:10 | WB05-INV01 | 100 | 2 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 12:00 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:05 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 12:10 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:15 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 12:20 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:25 | WB05-INV01 | 900 | 2 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 06:00 | WB05-INV02 | 100 | -80 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 06:05 | WB05-INV02 | 100 | -80 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 06:10 | WB05-INV02 | 100 | -80 | 1430 | 1430 | 1430 | 1430 | 0 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2
2026-05-14 12:00 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:05 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 12:10 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:15 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 12:20 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 13.1 | 13.1 | 13.1 | 13.1 | 0 | 13.1
2026-05-14 12:25 | WB05-INV02 | 900 | -80 | 1180 | 1180 | 1180 | 1180 | 0 | 1180 | 12.9 | 12.9 | 12.9 | 12.9 | 0 | 12.9
2026-05-14 06:00 | WB05-INV03 | 100 | 1 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 06:05 | WB05-INV03 | 100 | 1 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 06:10 | WB05-INV03 | 100 | 1 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 12:00 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:05 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9
2026-05-14 12:10 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:15 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9
2026-05-14 12:20 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:25 | WB05-INV03 | 900 | 1 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9
2026-05-14 06:00 | WB05-INV04 | 100 | -90 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 06:05 | WB05-INV04 | 100 | -90 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 06:10 | WB05-INV04 | 100 | -90 | 1430 | 1430 | 1100 | 1430 | 1430 | 1430 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
2026-05-14 12:00 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:05 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9
2026-05-14 12:10 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:15 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9
2026-05-14 12:20 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 13.1 | 13.1 | 14.3 | 13.1 | 13.1 | 13.1
2026-05-14 12:25 | WB05-INV04 | 900 | -90 | 1180 | 1180 | 1100 | 1180 | 1180 | 1180 | 12.9 | 12.9 | 14.1 | 12.9 | 12.9 | 12.9

## Helpers_GF
Helpers_GF — jembatan ground_fault.py (per-row)
daylight = (POA>thr & POA>floor). voc_cand = IF(¦I¦<0.5 & V>10, V, '') → Voc estimator (median nanti). peer_med_I PVk = MEDIAN arus 5 string LAIN (per baris). abs_Vgnd = ¦V_to_ground¦.
Production AND solar_elev>5° & inverter-shutdown (ephemeris, tak direplika statis); di sini daylight = baris noon.
Inverter_ID | Start Time | POA | daylight | V_gnd | voc_cand PV1 | voc_cand PV2 | voc_cand PV3 | voc_cand PV4 | voc_cand PV5 | voc_cand PV6 | peer_med_I PV1 | peer_med_I PV2 | peer_med_I PV3 | peer_med_I PV4 | peer_med_I PV5 | peer_med_I PV6 | abs_Vgnd

## GF_StringMetrics
GF_StringMetrics — per (inverter, PV string): Voc & peer-I z-score
voc_actual = MEDIAN(voc_cand) (hanya baris dawn I<0.5 non-blank). voc_ratio = voc_actual / voc_string_26_calc (1430.61V @30°C). i_z = (I_median_daylight − peer_med) / peer_std. spec_flag = voc_ratio<0.85 AND i_z>2 (string bukan-empty).
Inverter_ID | PV | is_empty | voc_actual (V) | voc_string_nominal (V) | voc_ratio | I_median_daylight | peer_med_daylight | peer_std_daylight | i_z | spec_flag
WB05-INV01 | PV1 | 0
WB05-INV01 | PV2 | 0
WB05-INV01 | PV3 | 0
WB05-INV01 | PV4 | 0
WB05-INV01 | PV5 | 1
WB05-INV01 | PV6 | 0
WB05-INV02 | PV1 | 0
WB05-INV02 | PV2 | 0
WB05-INV02 | PV3 | 0
WB05-INV02 | PV4 | 0
WB05-INV02 | PV5 | 1
WB05-INV02 | PV6 | 0
WB05-INV03 | PV1 | 0
WB05-INV03 | PV2 | 0
WB05-INV03 | PV3 | 0
WB05-INV03 | PV4 | 0
WB05-INV03 | PV5 | 0
WB05-INV03 | PV6 | 0
WB05-INV04 | PV1 | 0
WB05-INV04 | PV2 | 0
WB05-INV04 | PV3 | 0
WB05-INV04 | PV4 | 0
WB05-INV04 | PV5 | 0
WB05-INV04 | PV6 | 0

## M2c_GroundFault
M2c_GroundFault — keputusan per-inverter (ground_fault.py run())
Triple-signal: absolute(MAX¦V_gnd¦>50) · adaptive(¦med-fleet¦/std>3) · spec(ADA string voc_ratio<0.85 & i_z>2). confidence: spec+(abs¦adp)=90 · spec=80 · abs+adp=80 · abs=70 · adp=60. severity CRITICAL kalau conf≥80 else HIGH.
Finding per-inverter; pv_string = worst (voc_ratio terendah). value = ¦V_gnd_median¦. fleet median/std = INPUT (Config).
Inverter_ID | V_gnd_max_abs | V_gnd_median | adaptive_z | flag_absolute | flag_adaptive | flag_spec | triggered_by | confidence | severity | worst_PV | worst_voc_ratio | status | message
WB05-INV01
WB05-INV02
WB05-INV03
WB05-INV04

## M2c_GF_StringStatus
M2c_GF_StringStatus — replika artifact StringStatus (ground_fault.py)
Mirror self.artifacts['StringStatus']: per-PV status (fan-out status inverter), is_worst_string, V_gnd stats, confidence. Empty slot → EMPTY (top-up EmptyPVMap). Status string = status inverter (semua string inverter ter-flag dapat 'ground_fault').
poa_source | inverter_id | wb_id | pv_string | status | is_worst_string | v_gnd_median | v_gnd_max_abs | adaptive_z | triggered_by | confidence | voc_ratio
dummy_single | WB05-INV01 | WB05 | PV1
dummy_single | WB05-INV01 | WB05 | PV2
dummy_single | WB05-INV01 | WB05 | PV3
dummy_single | WB05-INV01 | WB05 | PV4
dummy_single | WB05-INV01 | WB05 | PV5 | EMPTY
dummy_single | WB05-INV01 | WB05 | PV6
dummy_single | WB05-INV02 | WB05 | PV1
dummy_single | WB05-INV02 | WB05 | PV2
dummy_single | WB05-INV02 | WB05 | PV3
dummy_single | WB05-INV02 | WB05 | PV4
dummy_single | WB05-INV02 | WB05 | PV5 | EMPTY
dummy_single | WB05-INV02 | WB05 | PV6
dummy_single | WB05-INV03 | WB05 | PV1
dummy_single | WB05-INV03 | WB05 | PV2
dummy_single | WB05-INV03 | WB05 | PV3
dummy_single | WB05-INV03 | WB05 | PV4
dummy_single | WB05-INV03 | WB05 | PV5
dummy_single | WB05-INV03 | WB05 | PV6
dummy_single | WB05-INV04 | WB05 | PV1
dummy_single | WB05-INV04 | WB05 | PV2
dummy_single | WB05-INV04 | WB05 | PV3
dummy_single | WB05-INV04 | WB05 | PV4
dummy_single | WB05-INV04 | WB05 | PV5
dummy_single | WB05-INV04 | WB05 | PV6

## Raw_Data_IF
Raw_Data_IF — V/I per PV string (WB05-INV01, 14 ts daylight)
1 inverter, 6 PV string, 14 timestamp noon (POA=900). Sel anomali di-inject (di-highlight): PV3@12:25/12:30 arus drop, PV5@12:45 V drop, PV2@12:10 arus tinggi.
Detector iForest ASLI train per inverter di SEMUA daylight sample. Ganti dengan data Huawei aktual (paste over).
t | Start Time | POA | PV1 V | PV2 V | PV3 V | PV4 V | PV5 V | PV6 V | PV1 I | PV2 I | PV3 I | PV4 I | PV5 I | PV6 I
0 | 46156.5 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.0897 | 9.9897 | 10.0697 | 10.0097 | 10.1097 | 9.9697
1 | 46156.5035 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1299 | 10.0299 | 10.1099 | 10.0499 | 10.1499 | 10.0099
2 | 46156.5069 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1665 | 12.6 | 10.1465 | 10.0865 | 10.1865 | 10.0465
3 | 46156.5104 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1979 | 10.0979 | 10.1779 | 10.1179 | 10.2179 | 10.0779
4 | 46156.5139 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.2228 | 10.1228 | 10.2028 | 10.1428 | 10.2428 | 10.1028
5 | 46156.5174 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.2401 | 10.1401 | 3 | 10.1601 | 10.2601 | 10.1201
6 | 46156.5208 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.2489 | 10.1489 | 4 | 10.1689 | 10.2689 | 10.1289
7 | 46156.5243 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.2489 | 10.1489 | 10.2289 | 10.1689 | 10.2689 | 10.1289
8 | 46156.5278 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.2401 | 10.1401 | 10.2201 | 10.1601 | 10.2601 | 10.1201
9 | 46156.5312 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1100 | 1199.1 | 10.2228 | 10.1228 | 10.2028 | 10.1428 | 10.2428 | 10.1028
10 | 46156.5347 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1979 | 10.0979 | 10.1779 | 10.1179 | 10.2179 | 10.0779
11 | 46156.5382 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1665 | 10.0665 | 10.1465 | 10.0865 | 10.1865 | 10.0465
12 | 46156.5417 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.1299 | 10.0299 | 10.1099 | 10.0499 | 10.1499 | 10.0099
13 | 46156.5451 | 900 | 1200.6 | 1199.4 | 1200.3 | 1199.7 | 1200.9 | 1199.1 | 10.0897 | 9.9897 | 10.0697 | 10.0097 | 10.1097 | 9.9697

## Features_IF
Features_IF — fitur build_feature_matrix + robust-z (MAD)
Fitur IDENTIK detector: V, I, V_dev=V−MEDIAN(siblings@ts), I_dev=I−MEDIAN(siblings@ts), R=V/MAX(I,floor). 84 sampel = 6 PV × 14 ts.
Skor A = MAX robust-z lintas 5 fitur, z=¦x−median¦/(1.4826·MAD) per fitur (stats kolom U-X). CATATAN: A ≈ proxy MAD, BUKAN skor IsolationForest asli (path-length 100 pohon).
pv | t | Start Time | V | I | V_dev | I_dev | R | absdev_V | absdev_I | absdev_Vdev | absdev_Idev | absdev_R | z_V | z_I | z_Vdev | z_Idev | z_R | A (max z) | feature | median | MAD | scale=1.4826·MAD
1 | 0 | [17 empty] | V
2 | 0 | [17 empty] | I
3 | 0 | [17 empty] | V_dev
4 | 0 | [17 empty] | I_dev
5 | 0 | [17 empty] | R
6 | 0
1 | 1
2 | 1
3 | 1
4 | 1
5 | 1
6 | 1
1 | 2
2 | 2
3 | 2
4 | 2
5 | 2
6 | 2
1 | 3
2 | 3
3 | 3
4 | 3
5 | 3
6 | 3
1 | 4
2 | 4
3 | 4
4 | 4
5 | 4
6 | 4
1 | 5
2 | 5
3 | 5
4 | 5
5 | 5
6 | 5
1 | 6
2 | 6
3 | 6
4 | 6
5 | 6
6 | 6
1 | 7
2 | 7
3 | 7
4 | 7
5 | 7
6 | 7
1 | 8
2 | 8
3 | 8
4 | 8
5 | 8
6 | 8
1 | 9
2 | 9
3 | 9
4 | 9
5 | 9
6 | 9
1 | 10
2 | 10
3 | 10
4 | 10
5 | 10
6 | 10
1 | 11
2 | 11
3 | 11
4 | 11
5 | 11
6 | 11
1 | 12
2 | 12
3 | 12
4 | 12
5 | 12
6 | 12
1 | 13
2 | 13
3 | 13
4 | 13
5 | 13
6 | 13

## IF_Anomaly
IF_Anomaly — flag contamination teratas + severity (kuartil) + confidence
threshold_A = PERCENTILE(A, 1−contamination). flag = A ≥ threshold. rank dalam flagged-set (A desc) → severity kuartil (≤25 CRITICAL, ≤50 HIGH, ≤75 MEDIUM, >75 INFO) — faithful _severity_from_quartile. confidence = 100−pct·0.5.
Severity & confidence FAITHFUL ke detector; tapi 'A' adalah skor MAD-approx, bukan IsolationForest. Sampel yang ditandai bisa BERBEDA dari iForest asli.
pv | t | Start Time | A | flag | rank_within_flagged | rank_pct | severity | confidence | metric | value
1 | 0 | [7 empty] | threshold_A
2 | 0 | [7 empty] | n_flagged
3 | 0 | [7 empty] | n_samples
4 | 0
5 | 0
6 | 0
1 | 1
2 | 1
3 | 1
4 | 1
5 | 1
6 | 1
1 | 2
2 | 2
3 | 2
4 | 2
5 | 2
6 | 2
1 | 3
2 | 3
3 | 3
4 | 3
5 | 3
6 | 3
1 | 4
2 | 4
3 | 4
4 | 4
5 | 4
6 | 4
1 | 5
2 | 5
3 | 5
4 | 5
5 | 5
6 | 5
1 | 6
2 | 6
3 | 6
4 | 6
5 | 6
6 | 6
1 | 7
2 | 7
3 | 7
4 | 7
5 | 7
6 | 7
1 | 8
2 | 8
3 | 8
4 | 8
5 | 8
6 | 8
1 | 9
2 | 9
3 | 9
4 | 9
5 | 9
6 | 9
1 | 10
2 | 10
3 | 10
4 | 10
5 | 10
6 | 10
1 | 11
2 | 11
3 | 11
4 | 11
5 | 11
6 | 11
1 | 12
2 | 12
3 | 12
4 | 12
5 | 12
6 | 12
1 | 13
2 | 13
3 | 13
4 | 13
5 | 13
6 | 13

## IF_Summary
IF_Summary — ringkasan per inverter (approx)
Mirror artifact AnomalySummary. n_flagged ≈ contamination × n_samples (PERCENTILE boundary + ties).
inverter_id | n_samples | n_flagged | flagged_pct | threshold_A | max_A | min_A
WB05-INV01

## Raw_Data_LI
Raw_Data_LI -- POA, elevasi matahari & daya inverter per timestamp (SINTETIS)
WB05, 6 inverter, satu hari @5 menit; awan 11:00-13:00 (POA ~150, matahari tinggi). P = sum daya per-PV (kW). Sel kosong = tidak ada data (INV06 saat POA < 250).
Skenario: semua x0,93 di cahaya rendah (cuaca, tidak di-flag); INV03 x0,83 lagi (cacat low-light); INV05 x0,80 hanya saat elevasi < 30 derajat (bayangan pagi/sore).
Ganti dengan data Huawei aktual satu WB (paste over): semua inverter WB berbagi POA WS yang sama.
timestamp | POA (W/m²) | elev (°) | WB05-INV01 P (kW) | WB05-INV02 P (kW) | WB05-INV03 P (kW) | WB05-INV04 P (kW) | WB05-INV05 P (kW) | WB05-INV06 P (kW)
2026-05-14 06:30 | 17.0371 | 11.0947 | 1.7576 | 1.9186 | 1.712 | 2.2014 | 1.8831
2026-05-14 06:35 | 23.1415 | 12.9305 | 2.3906 | 2.6006 | 2.3169 | 2.9846 | 2.5622
2026-05-14 06:40 | 30.1537 | 14.7601 | 3.1151 | 3.3783 | 3.0088 | 3.8868 | 3.3478
2026-05-14 06:45 | 38.0602 | 16.5827 | 3.927 | 4.2489 | 3.7878 | 4.9098 | 4.2402
2026-05-14 06:50 | 46.8461 | 18.3974 | 4.8218 | 5.2107 | 4.6551 | 6.0555 | 5.2382
2026-05-14 06:55 | 56.4946 | 20.2033 | 5.796 | 6.2638 | 5.6129 | 7.3247 | 6.3386
2026-05-14 07:00 | 66.9873 | 21.9996 | 6.8474 | 7.4099 | 6.6632 | 8.7162 | 7.536
2026-05-14 07:05 | 78.3043 | 23.7855 | 7.9758 | 8.652 | 7.8074 | 10.226 | 8.8231
2026-05-14 07:10 | 90.424 | 25.56 | 9.1828 | 9.9935 | 9.045 | 11.8469 | 10.1917
2026-05-14 07:15 | 103.3233 | 27.3224 | 10.4719 | 11.4369 | 10.373 | 13.5692 | 11.6334
2026-05-14 07:20 | 116.9778 | 29.0717 | 11.8472 | 12.9828 | 11.7859 | 15.381 | 13.1413
2026-05-14 07:25 | 131.3613 | 30.8072 | 13.3124 | 14.6289 | 13.2751 | 17.2703 | 18.3886
2026-05-14 07:30 | 146.4466 | 32.5281 | 14.8696 | 16.369 | 14.83 | 19.2262 | 20.4262
2026-05-14 07:35 | 162.2049 | 34.2335 | 16.5179 | 18.1931 | 16.4394 | 21.2409 | 22.5426
2026-05-14 07:40 | 178.6062 | 35.9226 | 18.2526 | 20.0882 | 18.0924 | 23.3109 | 24.7448
2026-05-14 07:45 | 195.6193 | 37.5945 | 20.0646 | 22.0394 | 19.7804 | 25.4378 | 27.0426
2026-05-14 07:50 | 213.2118 | 39.2486 | 21.9413 | 24.0319 | 21.4986 | 27.6283 | 29.4465
2026-05-14 07:55 | 231.3502 | 40.884 | 23.8671 | 26.0527 | 23.2465 | 29.8925 | 31.9645
2026-05-14 08:00 | 250 | 42.5 | 25.826 | 28.0932 | 25.0283 | 32.2427 | 34.6004
2026-05-14 08:05 | 269.1257 | 44.0957 | 29.8953 | 32.4193 | 34.7873 | 37.301 | 40.1626 | 43.2527
2026-05-14 08:10 | 288.6909 | 45.6705 | 32.0274 | 34.6515 | 37.2191 | 40.0452 | 43.2319 | 46.5325
2026-05-14 08:15 | 308.6583 | 47.2235 | 34.1592 | 36.9137 | 39.7345 | 42.9033 | 46.3924 | 49.8463
2026-05-14 08:20 | 328.9899 | 48.754 | 36.2906 | 39.2199 | 42.3455 | 45.8681 | 49.6163 | 53.1648
2026-05-14 08:25 | 349.6471 | 50.2613 | 38.4284 | 41.5866 | 45.0584 | 48.923 | 52.8717 | 56.4645
2026-05-14 08:30 | 370.5905 | 51.7447 | 40.5857 | 44.0291 | 47.8714 | 52.0427 | 56.1262 | 59.7312
2026-05-14 08:35 | 391.7802 | 53.2035 | 42.7792 | 46.5586 | 50.773 | 55.1957 | 59.351 | 62.962
2026-05-14 08:40 | 413.1759 | 54.6369 | 45.0265 | 49.1789 | 53.7417 | 58.3474 | 62.5253 | 66.1662
2026-05-14 08:45 | 434.7369 | 56.0444 | 47.3429 | 51.8841 | 56.7481 | 61.4652 | 65.6395 | 69.3643
2026-05-14 08:50 | 456.4221 | 57.4252 | 49.7373 | 54.6584 | 59.7579 | 64.5223 | 68.6968 | 72.5844
2026-05-14 08:55 | 478.1903 | 58.7786 | 52.2105 | 57.4763 | 62.7356 | 67.5019 | 71.7127 | 75.8577
2026-05-14 09:00 | 500 | 60.1041 | 54.7527 | 60.3052 | 65.6496 | 70.3998 | 74.7134 | 79.2127
2026-05-14 09:05 | 521.8097 | 61.4009 | 57.3438 | 63.1091 | 68.4764 | 73.2256 | 77.7311 | 82.6699
2026-05-14 09:10 | 543.5779 | 62.6686 | 59.9551 | 65.853 | 71.2043 | 76.0007 | 80.7985 | 86.2362
2026-05-14 09:15 | 565.2631 | 63.9064 | 62.5521 | 68.5081 | 73.8352 | 78.756 | 83.9436 | 89.9023
2026-05-14 09:20 | 586.8241 | 65.1138 | 65.0985 | 71.0552 | 76.3845 | 81.5264 | 87.183 | 93.6418
2026-05-14 09:25 | 608.2198 | 66.2902 | 67.5615 | 73.4881 | 78.8791 | 84.3449 | 90.5186 | 97.4128
2026-05-14 09:30 | 629.4095 | 67.435 | 69.9159 | 75.8149 | 81.3531 | 87.2369 | 93.9345 | 101.162
2026-05-14 09:35 | 650.3529 | 68.5478 | 72.1476 | 78.0564 | 83.8428 | 90.2148 | 97.3979 | 104.8316
2026-05-14 09:40 | 671.0101 | 69.6279 | 74.2566 | 80.2436 | 86.3798 | 93.2744 | 100.8618 | 108.3663
2026-05-14 09:45 | 691.3417 | 70.6749 | 76.2563 | 82.4127 | 88.9859 | 96.3936 | 104.27 | 111.7208
2026-05-14 09:50 | 711.3091 | 71.6883 | 78.1721 | 84.5995 | 91.6683 | 99.5339 | 107.5645 | 114.8665
2026-05-14 09:55 | 730.8743 | 72.6675 | 80.0378 | 86.833 | 94.4165 | 102.6447 | 110.6933 | 117.7958
2026-05-14 10:00 | 750 | 73.6122 | 81.8901 | 89.1305 | 97.203 | 105.6687 | 113.617 | 120.5232
2026-05-14 10:05 | 768.6498 | 74.5218 | 83.7628 | 91.4933 | 99.9848 | 108.55 | 116.315 | 123.0837
2026-05-14 10:10 | 786.7882 | 75.3959 | 85.6812 | 93.9054 | 102.7093 | 111.241 | 118.7885 | 125.5275
2026-05-14 10:15 | 804.3807 | 76.2342 | 87.6573 | 96.3343 | 105.32 | 113.7099 | 121.0608 | 127.913
2026-05-14 10:20 | 821.3938 | 77.0362 | 89.6868 | 98.7344 | 107.7646 | 115.9445 | 123.1735 | 130.2971
2026-05-14 10:25 | 837.7951 | 77.8015 | 91.7487 | 101.0527 | 110.002 | 117.9547 | 125.1812 | 132.7265
2026-05-14 10:30 | 853.5534 | 78.5298 | 93.8069 | 103.2353 | 112.0082 | 119.7712 | 127.1428 | 135.2296
2026-05-14 10:35 | 868.6387 | 79.2207 | 95.8147 | 105.2354 | 113.7797 | 121.4411 | 129.1125 | 137.8106
2026-05-14 10:40 | 883.0222 | 79.8739 | 97.7206 | 107.0189 | 115.3343 | 123.0209 | 131.1313 | 140.4481
2026-05-14 10:45 | 896.6767 | 80.4891 | 99.4751 | 108.5703 | 116.7088 | 124.5681 | 133.2198 | 143.0956
2026-05-14 10:50 | 909.576 | 81.0659 | 101.0377 | 109.894 | 117.9537 | 126.1327 | 135.3738 | 145.688
2026-05-14 10:55 | 921.6957 | 81.6042 | 102.3822 | 111.0149 | 119.1254 | 127.7485 | 137.5641 | 148.1487
2026-05-14 11:00 | 127.6484 | 82.1037 | 13.1691 | 14.2472 | 12.7021 | 16.4679 | 17.7799
2026-05-14 11:05 | 110.0098 | 82.5641 | 11.3213 | 12.234 | 10.9312 | 14.2223 | 15.3794
2026-05-14 11:10 | 129.138 | 82.9852 | 13.2462 | 14.3158 | 12.8306 | 16.7463 | 18.1146
2026-05-14 11:15 | 167.4466 | 83.3667 | 17.1129 | 18.5206 | 16.6576 | 21.7922 | 23.5498
2026-05-14 11:20 | 189.7149 | 83.7087 | 19.3201 | 20.9616 | 18.9187 | 24.7803 | 26.7221
2026-05-14 11:25 | 175.4695 | 84.0107 | 17.817 | 19.3936 | 17.5553 | 22.9928 | 24.7208
2026-05-14 11:30 | 137.8076 | 84.2728 | 13.9659 | 15.2558 | 13.8379 | 18.0997 | 19.3932
2026-05-14 11:35 | 111.3553 | 84.4948 | 11.2777 | 12.361 | 11.2215 | 14.6422 | 15.6346
2026-05-14 11:40 | 120.4328 | 84.6765 | 12.2058 | 13.4146 | 12.1724 | 15.8328 | 16.8555
2026-05-14 11:45 | 156.6942 | 84.818 | 15.9123 | 17.5179 | 15.869 | 20.5692 | 21.8511
2026-05-14 11:50 | 186.801 | 84.9191 | 19.0262 | 20.9555 | 18.9323 | 24.4577 | 25.9559
2026-05-14 11:55 | 183.0731 | 84.9798 | 18.7129 | 20.5932 | 18.5436 | 23.8891 | 25.3599
2026-05-14 12:00 | 148.938 | 85 | 15.2795 | 16.7811 | 15.0582 | 19.3636 | 20.5876
2026-05-14 12:05 | 115.7792 | 84.9798 | 11.9166 | 13.0497 | 11.6722 | 15.0001 | 15.9899
2026-05-14 12:10 | 114.0829 | 84.9191 | 11.7706 | 12.8459 | 11.4609 | 14.7386 | 15.7632
2026-05-14 12:15 | 145.4086 | 84.818 | 15.0218 | 16.3375 | 14.5544 | 18.7522 | 20.1274
2026-05-14 12:20 | 180.9556 | 84.6765 | 18.6933 | 20.2685 | 18.052 | 23.3252 | 25.1188
2026-05-14 12:25 | 188.0422 | 84.4948 | 19.399 | 20.9864 | 18.7111 | 24.26 | 26.1937
2026-05-14 12:30 | 160.1529 | 84.2728 | 16.4807 | 17.8092 | 15.9135 | 20.7059 | 22.391
2026-05-14 12:35 | 122.9291 | 84.0107 | 12.6085 | 13.6268 | 12.2139 | 15.9422 | 17.2446
2026-05-14 12:40 | 110.5941 | 83.7087 | 11.3018 | 12.232 | 11.0023 | 14.3942 | 15.5546
2026-05-14 12:45 | 134.4887 | 83.3667 | 13.6952 | 14.8595 | 13.4122 | 17.5678 | 18.9436
2026-05-14 12:50 | 172.6443 | 82.9852 | 17.5293 | 19.0817 | 17.2738 | 22.6238 | 24.3226
2026-05-14 12:55 | 189.9808 | 82.5641 | 19.2528 | 21.0324 | 19.0781 | 24.953 | 26.7345
2026-05-14 13:00 | 933.0127 | 82.1037 | 101.6052 | 111.3707 | 121.8127 | 131.9175 | 140.8508 | 148.8373
2026-05-14 13:05 | 921.6957 | 81.6042 | 100.4468 | 110.399 | 120.6916 | 130.2898 | 138.6991 | 146.5527
2026-05-14 13:10 | 909.576 | 81.0659 | 99.3246 | 109.3489 | 119.34 | 128.382 | 136.3785 | 144.2753
2026-05-14 13:15 | 896.6767 | 80.4891 | 98.209 | 108.1674 | 117.7335 | 126.2306 | 133.9623 | 142.0515
2026-05-14 13:20 | 883.0222 | 79.8739 | 97.0588 | 106.8083 | 115.8699 | 123.8899 | 131.5195 | 139.9023
2026-05-14 13:25 | 868.6387 | 79.2207 | 95.8272 | 105.2394 | 113.7695 | 121.4247 | 129.1052 | 137.8209
2026-05-14 13:30 | 853.5534 | 78.5298 | 94.4696 | 103.4462 | 111.4719 | 118.9011 | 126.7542 | 135.776
2026-05-14 13:35 | 837.7951 | 77.8015 | 92.9495 | 101.4348 | 109.0302 | 116.378 | 124.477 | 133.7167
2026-05-14 13:40 | 821.3938 | 77.0362 | 91.2443 | 99.2301 | 106.5041 | 113.8994 | 122.2601 | 131.5815
2026-05-14 13:45 | 804.3807 | 76.2342 | 89.3485 | 96.8725 | 103.9513 | 111.4893 | 120.069 | 129.3076
2026-05-14 13:50 | 786.7882 | 75.3959 | 87.2738 | 94.4122 | 101.4204 | 109.1499 | 117.8546 | 126.8409
2026-05-14 13:55 | 768.6498 | 74.5218 | 85.0479 | 91.9023 | 98.9448 | 106.8625 | 115.5613 | 124.1434
2026-05-14 14:00 | 750 | 73.6122 | 82.7101 | 89.3915 | 96.5393 | 104.592 | 113.136 | 121.1995
2026-05-14 14:05 | 730.8743 | 72.6675 | 80.3059 | 86.9184 | 94.1995 | 102.2926 | 110.536 | 118.0169
2026-05-14 14:10 | 711.3091 | 71.6883 | 77.881 | 84.5069 | 91.9039 | 99.9162 | 107.7353 | 114.6264
2026-05-14 14:15 | 691.3417 | 70.6749 | 75.475 | 82.1641 | 89.6182 | 97.4194 | 104.7281 | 111.0765
2026-05-14 14:20 | 671.0101 | 69.6279 | 73.1173 | 79.881 | 87.3018 | 94.7703 | 101.5299 | 107.4267
2026-05-14 14:25 | 650.3529 | 68.5478 | 70.8236 | 77.635 | 84.9143 | 91.9534 | 98.1744 | 103.7397
2026-05-14 14:30 | 629.4095 | 67.435 | 68.5951 | 75.3946 | 82.422 | 88.9711 | 94.709 | 100.0728
2026-05-14 14:35 | 608.2198 | 66.2902 | 66.42 | 73.1249 | 79.8029 | 85.8438 | 91.188 | 96.4714
2026-05-14 14:40 | 586.8241 | 65.1138 | 64.2762 | 70.7935 | 77.05 | 82.6061 | 87.6653 | 92.9637
2026-05-14 14:45 | 565.2631 | 63.9064 | 62.136 | 68.3757 | 74.1719 | 79.3023 | 84.1876 | 89.5592
2026-05-14 14:50 | 543.5779 | 62.6686 | 59.9708 | 65.858 | 71.1917 | 75.9802 | 80.7894 | 86.249
2026-05-14 14:55 | 521.8097 | 61.4009 | 57.7559 | 63.2402 | 68.1429 | 72.6845 | 77.4894 | 83.0097
2026-05-14 15:00 | 500 | 60.1041 | 55.4746 | 60.5349 | 65.0653 | 69.452 | 74.2901 | 79.8081
2026-05-14 15:05 | 478.1903 | 58.7786 | 53.1202 | 57.7658 | 61.9993 | 66.3074 | 71.1792 | 76.6079
2026-05-14 15:10 | 456.4221 | 57.4252 | 50.6975 | 54.964 | 58.9809 | 63.2616 | 68.1337 | 73.3762
2026-05-14 15:15 | 434.7369 | 56.0444 | 48.221 | 52.1636 | 56.0374 | 60.3121 | 65.1245 | 70.0885
2026-05-14 15:20 | 413.1759 | 54.6369 | 45.7137 | 49.3975 | 53.1856 | 57.4452 | 62.1223 | 66.7329
2026-05-14 15:25 | 391.7802 | 53.2035 | 43.2027 | 46.6934 | 50.4302 | 54.6395 | 59.1026 | 63.3113
2026-05-14 15:30 | 370.5905 | 51.7447 | 40.7164 | 44.0707 | 47.7657 | 51.8711 | 56.0495 | 59.839
2026-05-14 15:35 | 349.6471 | 50.2613 | 38.2804 | 41.5395 | 45.1782 | 49.1174 | 52.9585 | 56.3425
2026-05-14 15:40 | 328.9899 | 48.754 | 35.9148 | 39.1003 | 42.6496 | 46.3615 | 49.8367 | 52.8549
2026-05-14 15:45 | 308.6583 | 47.2235 | 33.6325 | 36.746 | 40.1607 | 43.5948 | 46.7012 | 49.4119
2026-05-14 15:50 | 288.6909 | 45.6705 | 31.4386 | 34.4641 | 37.6957 | 40.8183 | 43.5772 | 46.0469
2026-05-14 15:55 | 269.1257 | 44.0957 | 29.331 | 32.2397 | 35.244 | 38.042 | 40.4935 | 42.7873
2026-05-14 16:00 | 250 | 42.5 | 25.3911 | 27.9548 | 25.3204 | 32.8136 | 34.8554
2026-05-14 16:05 | 231.3502 | 40.884 | 23.568 | 25.9575 | 23.4474 | 30.2853 | 32.14
2026-05-14 16:10 | 213.2118 | 39.2486 | 21.798 | 23.9863 | 21.5949 | 27.8164 | 29.5305
2026-05-14 16:15 | 195.6193 | 37.5945 | 20.0725 | 22.0419 | 19.7752 | 25.4275 | 27.038
2026-05-14 16:20 | 178.6062 | 35.9226 | 18.386 | 20.1306 | 18.0028 | 23.1357 | 24.6666
2026-05-14 16:25 | 162.2049 | 34.2335 | 16.7373 | 18.2629 | 16.292 | 20.9528 | 22.4139
2026-05-14 16:30 | 146.4466 | 32.5281 | 15.1296 | 16.4517 | 14.6554 | 18.8849 | 20.2738
2026-05-14 16:35 | 131.3613 | 30.8072 | 13.5695 | 14.7107 | 13.1024 | 16.9327 | 18.2378
2026-05-14 16:40 | 116.9778 | 29.0717 | 12.0665 | 13.0526 | 11.6386 | 15.0931 | 13.0384
2026-05-14 16:45 | 103.3233 | 27.3224 | 10.6309 | 11.4875 | 10.2663 | 13.3605 | 11.5588
2026-05-14 16:50 | 90.424 | 25.56 | 9.2727 | 10.0221 | 8.9846 | 11.7289 | 10.1495
2026-05-14 16:55 | 78.3043 | 23.7855 | 8.0005 | 8.6599 | 7.7908 | 10.1936 | 8.8116
2026-05-14 17:00 | 66.9873 | 21.9996 | 6.8202 | 7.4012 | 6.6815 | 8.752 | 7.5488
2026-05-14 17:05 | 56.4946 | 20.2033 | 5.7354 | 6.2445 | 5.6536 | 7.4043 | 6.3671
2026-05-14 17:10 | 46.8461 | 18.3974 | 4.7471 | 5.1869 | 4.7053 | 6.1536 | 5.2733
2026-05-14 17:15 | 38.0602 | 16.5827 | 3.8547 | 4.2258 | 3.8363 | 5.0047 | 4.2741
2026-05-14 17:20 | 30.1537 | 14.7601 | 3.0564 | 3.3596 | 3.0483 | 3.9639 | 3.3753
2026-05-14 17:25 | 23.1415 | 12.9305 | 2.3505 | 2.5878 | 2.3439 | 3.0373 | 2.581
2026-05-14 17:30 | 17.0371 | 11.0947 | 1.7357 | 1.9117 | 1.7267 | 2.2301 | 1.8934

## Helpers_LI
Helpers_LI -- efisiensi relatif & deviasi terhadap median tetangga se-WB
pr=P/POA; midpr=pr bila POA di pita menengah; e=pr/median(midpr) (baris 5) bila n_mid (baris 4) >= min; peer=MEDIAN(e) bila COUNT >= min_peers; dev=e/peer; lowdev=dev bila pita rendah & elevasi >= batas.
Sel "" = tidak ada nilai; MEDIAN/COUNT mengabaikannya (sama dengan NaN di Python).
n_mid
median mid
timestamp | POA | elev | in_mid | in_low_hs | pr_1 | pr_2 | pr_3 | pr_4 | pr_5 | pr_6 | midpr_1 | midpr_2 | midpr_3 | midpr_4 | midpr_5 | midpr_6 | e_1 | e_2 | e_3 | e_4 | e_5 | e_6 | n_peers | peer_median | dev_1 | dev_2 | dev_3 | dev_4 | dev_5 | dev_6 | lowdev_1 | lowdev_2 | lowdev_3 | lowdev_4 | lowdev_5 | lowdev_6

## M2a_LowIrradiance
M2a_LowIrradiance -- low_ratio relatif tetangga se-WB + robust z + klasifikasi
low_ratio = MEDIAN(lowdev); median & MAD atas inverter terevaluasi; z = (low_ratio - median) / (1.4826 x MAX(MAD, 0.005)).
Flag bila low_ratio < cfg_li_low_ratio_threshold DAN z < -cfg_li_robust_z_min. Severity: < 0,80 CRITICAL; < 0,85 HIGH; lainnya MEDIUM.
inverter_id | n_mid | median_mid_pr | n_low | evaluated | low_ratio | wb_median_low_ratio | abs_dev | mad | robust_z | classification | severity | emit | confidence | message
WB05-INV01
WB05-INV02
WB05-INV03
WB05-INV04
WB05-INV05
WB05-INV06

## LI_Summary
LI_Summary -- hitung per klasifikasi (mirror LowIrradianceSummary)
general_underperform tidak lagi dihasilkan sejak 2026-09-28; baris dipertahankan (selalu 0) supaya dasbor lama tidak rusak.
classification | count
low_irradiance_underperform
general_underperform
normal
insufficient_data
n_emit

## Raw_Data_SH
Raw_Data_SH — daya per-PV (kW) + POA per timestamp (WB05-INV01)
1 inverter, 6 PV, 8 jam (08:00–15:00) × 6 timestamp/jam = 48 baris. Jam 8/9/10 di-shade (di-highlight): daya turun seragam → CV rendah + PR rendah.
Daya per-PV = Σ source PV{n} Power(kW) (atau V·I/1000). Ganti dengan data Huawei aktual (paste over).
inverter_id | hour | Start Time | POA (W/m²) | PV1 Power(kW) | PV2 Power(kW) | PV3 Power(kW) | PV4 Power(kW) | PV5 Power(kW) | PV6 Power(kW)
WB05-INV01 | 8 | 46156.3333 | 339.5 | 0.56583 | 0.57715 | 0.55452 | 0.57149 | 0.56017 | 0.56583
WB05-INV01 | 8 | 46156.3403 | 346.5 | 0.5775 | 0.58905 | 0.56595 | 0.58327 | 0.57172 | 0.5775
WB05-INV01 | 8 | 46156.3472 | 350 | 0.58333 | 0.595 | 0.57167 | 0.58917 | 0.5775 | 0.58333
WB05-INV01 | 8 | 46156.3542 | 353.5 | 0.58917 | 0.60095 | 0.57738 | 0.59506 | 0.58327 | 0.58917
WB05-INV01 | 8 | 46156.3611 | 350 | 0.58333 | 0.595 | 0.57167 | 0.58917 | 0.5775 | 0.58333
WB05-INV01 | 8 | 46156.3681 | 360.5 | 0.60083 | 0.61285 | 0.58882 | 0.60684 | 0.59483 | 0.60083
WB05-INV01 | 9 | 46156.375 | 533.5 | 0.88917 | 0.90695 | 0.87138 | 0.89806 | 0.88028 | 0.88917
WB05-INV01 | 9 | 46156.3819 | 544.5 | 0.9075 | 0.92565 | 0.88935 | 0.91658 | 0.89843 | 0.9075
WB05-INV01 | 9 | 46156.3889 | 550 | 0.91667 | 0.935 | 0.89833 | 0.92583 | 0.9075 | 0.91667
WB05-INV01 | 9 | 46156.3958 | 555.5 | 0.92583 | 0.94435 | 0.90732 | 0.93509 | 0.91657 | 0.92583
WB05-INV01 | 9 | 46156.4028 | 550 | 0.91667 | 0.935 | 0.89833 | 0.92583 | 0.9075 | 0.91667
WB05-INV01 | 9 | 46156.4097 | 566.5 | 0.94417 | 0.96305 | 0.92528 | 0.95361 | 0.93472 | 0.94417
WB05-INV01 | 10 | 46156.4167 | 698.4 | 1.164 | 1.1873 | 1.1407 | 1.1756 | 1.1524 | 1.164
WB05-INV01 | 10 | 46156.4236 | 712.8 | 1.188 | 1.2118 | 1.1642 | 1.1999 | 1.1761 | 1.188
WB05-INV01 | 10 | 46156.4306 | 720 | 1.2 | 1.224 | 1.176 | 1.212 | 1.188 | 1.2
WB05-INV01 | 10 | 46156.4375 | 727.2 | 1.212 | 1.2362 | 1.1878 | 1.2241 | 1.1999 | 1.212
WB05-INV01 | 10 | 46156.4444 | 720 | 1.2 | 1.224 | 1.176 | 1.212 | 1.188 | 1.2
WB05-INV01 | 10 | 46156.4514 | 741.6 | 1.236 | 1.2607 | 1.2113 | 1.2484 | 1.2236 | 1.236
WB05-INV01 | 11 | 46156.4583 | 824.5 | 2.7483 | 3.0232 | 2.4735 | 2.8857 | 2.6109 | 2.7483
WB05-INV01 | 11 | 46156.4653 | 841.5 | 2.805 | 3.0855 | 2.5245 | 2.9453 | 2.6648 | 2.805
WB05-INV01 | 11 | 46156.4722 | 850 | 2.8333 | 3.1167 | 2.55 | 2.975 | 2.6917 | 2.8333
WB05-INV01 | 11 | 46156.4792 | 858.5 | 2.8617 | 3.1478 | 2.5755 | 3.0048 | 2.7186 | 2.8617
WB05-INV01 | 11 | 46156.4861 | 850 | 2.8333 | 3.1167 | 2.55 | 2.975 | 2.6917 | 2.8333
WB05-INV01 | 11 | 46156.4931 | 875.5 | 2.9183 | 3.2102 | 2.6265 | 3.0643 | 2.7724 | 2.9183
WB05-INV01 | 12 | 46156.5 | 873 | 2.91 | 3.201 | 2.619 | 3.0555 | 2.7645 | 2.91
WB05-INV01 | 12 | 46156.5069 | 891 | 2.97 | 3.267 | 2.673 | 3.1185 | 2.8215 | 2.97
WB05-INV01 | 12 | 46156.5139 | 900 | 3 | 3.3 | 2.7 | 3.15 | 2.85 | 3
WB05-INV01 | 12 | 46156.5208 | 909 | 3.03 | 3.333 | 2.727 | 3.1815 | 2.8785 | 3.03
WB05-INV01 | 12 | 46156.5278 | 900 | 3 | 3.3 | 2.7 | 3.15 | 2.85 | 3
WB05-INV01 | 12 | 46156.5347 | 927 | 3.09 | 3.399 | 2.781 | 3.2445 | 2.9355 | 3.09
WB05-INV01 | 13 | 46156.5417 | 795.4 | 2.6513 | 2.9165 | 2.3862 | 2.7839 | 2.5188 | 2.6513
WB05-INV01 | 13 | 46156.5486 | 811.8 | 2.706 | 2.9766 | 2.4354 | 2.8413 | 2.5707 | 2.706
WB05-INV01 | 13 | 46156.5556 | 820 | 2.7333 | 3.0067 | 2.46 | 2.87 | 2.5967 | 2.7333
WB05-INV01 | 13 | 46156.5625 | 828.2 | 2.7607 | 3.0367 | 2.4846 | 2.8987 | 2.6226 | 2.7607
WB05-INV01 | 13 | 46156.5694 | 820 | 2.7333 | 3.0067 | 2.46 | 2.87 | 2.5967 | 2.7333
WB05-INV01 | 13 | 46156.5764 | 844.6 | 2.8153 | 3.0969 | 2.5338 | 2.9561 | 2.6746 | 2.8153
WB05-INV01 | 14 | 46156.5833 | 630.5 | 2.1017 | 2.3118 | 1.8915 | 2.2067 | 1.9966 | 2.1017
WB05-INV01 | 14 | 46156.5903 | 643.5 | 2.145 | 2.3595 | 1.9305 | 2.2523 | 2.0377 | 2.145
WB05-INV01 | 14 | 46156.5972 | 650 | 2.1667 | 2.3833 | 1.95 | 2.275 | 2.0583 | 2.1667
WB05-INV01 | 14 | 46156.6042 | 656.5 | 2.1883 | 2.4072 | 1.9695 | 2.2978 | 2.0789 | 2.1883
WB05-INV01 | 14 | 46156.6111 | 650 | 2.1667 | 2.3833 | 1.95 | 2.275 | 2.0583 | 2.1667
WB05-INV01 | 14 | 46156.6181 | 669.5 | 2.2317 | 2.4548 | 2.0085 | 2.3432 | 2.1201 | 2.2317
WB05-INV01 | 15 | 46156.625 | 436.5 | 1.455 | 1.6005 | 1.3095 | 1.5277 | 1.3822 | 1.455
WB05-INV01 | 15 | 46156.6319 | 445.5 | 1.485 | 1.6335 | 1.3365 | 1.5593 | 1.4107 | 1.485
WB05-INV01 | 15 | 46156.6389 | 450 | 1.5 | 1.65 | 1.35 | 1.575 | 1.425 | 1.5
WB05-INV01 | 15 | 46156.6458 | 454.5 | 1.515 | 1.6665 | 1.3635 | 1.5908 | 1.4392 | 1.515
WB05-INV01 | 15 | 46156.6528 | 450 | 1.5 | 1.65 | 1.35 | 1.575 | 1.425 | 1.5
WB05-INV01 | 15 | 46156.6597 | 463.5 | 1.545 | 1.6995 | 1.3905 | 1.6222 | 1.4678 | 1.545

## Helpers_SH
Helpers_SH — per timestamp: inv_total + CV antar PV
inv_total = Σ daya PV. CV_ts = STDEVP(daya PV)/AVERAGE(daya PV) — variasi antar string (uniform shading → CV kecil).
Production pakai hanya daya finite & >0 (di sini semua positif). cv_hour = MEDIAN(CV_ts) dihitung di SH_Hourly.
hour | Start Time | POA | inv_total (kW) | CV_ts

## SH_Hourly
SH_Hourly — agregat per jam: cv_hour, pr_proxy, suspicious
cv_hour = MEDIAN(CV_ts dlm jam). pr_proxy = AVERAGE(inv_total)/AVERAGE(POA) dlm jam. suspicious = cv_hour < cv_threshold DAN pr_proxy < pr_threshold (threshold di M2a_Shading).
hour | AM/PM | cv_hour | pr_proxy | mean_POA | mean_inv | n_samples | suspicious
8
9
10
11
12
13
14
15

## M2a_Shading
M2a_Shading — keputusan per inverter (median ref + asimetri diurnal)
cv_median/pr_median = MEDIAN cv_hour/pr_proxy lintas jam. threshold = mult·median. asimetri AM/PM membedakan terrain shadow (asimetris) vs soiling/awan (uniform). severity = frac·0.7 + asim·0.3.
IKN: lat −0.99, panel hadap utara → performa AM≈PM saat normal; suspicious terkonsentrasi AM/PM = sinyal shading terrain.
metric | value
cv_median
pr_median
cv_threshold
pr_threshold
total_hours
n_suspicious
n_am
n_pm
asymmetry
fault_type
frac_suspicious
score
severity
confidence

## Raw_Data_SO
Raw_Data_SO — energi & insolasi harian site (12 hari demo)
energy_daily (kWh) = Σ daya inverter × Δt (Riemann). insolation_daily (kWh/m²) = Σ POA/1000 × Δt. Production butuh ≥90 hari (SRR); 12 hari di sini hanya ilustrasi metrik PR harian.
Bangun dari pv_pipeline.baseline.BaselineAccumulator (simpan data NORMAL harian). Ganti dengan data aktual.
date | energy_daily (kWh) | insolation_daily (kWh/m²)
2026-02-01 | 310000 | 5.4
2026-02-02 | 318000 | 5.5
2026-02-03 | 305000 | 5.3
2026-02-04 | 322000 | 5.6
2026-02-05 | 315000 | 5.5
2026-02-06 | 308000 | 5.35
2026-02-07 | 320000 | 5.55
2026-02-08 | 312000 | 5.45
2026-02-09 | 317000 | 5.5
2026-02-10 | 309000 | 5.4
2026-02-11 | 314000 | 5.45
2026-02-12 | 321000 | 5.6

## Helpers_SO
Helpers_SO — PR harian (IEC 61724-1) + avg_daily_kwh
PR_daily = energy_daily / (insolation_daily × capacity_kwp). avg_daily_kwh = AVERAGE(energy) (proxy tail-30 hari).
date | energy_daily | insolation_daily | PR_daily
avg_daily_kwh
PR_mean
n_days_sample

## SO_Economics
SO_Economics — kalkulator cleaning ROI (hilir SRR; LIVE)
soiling_ratio (sr) = OUTPUT rdtools.soiling_srr() Monte-Carlo — INPUT di sini (di-highlight), TIDAK dihitung Excel.
Hilir sr SEMUA live: p_loss=1−sr; daily_loss=avg_daily_kwh·tarif·p_loss; payback=biaya/daily_loss; severity & recommend.
avg_daily_kwh (dari Helpers)
n_days_assumed | 120
data_status (gate)
cleaning_cost_idr / tariff / payback_thr
soiling_ratio (sr) [INPUT] | p_loss | daily_loss_idr | payback_days | recommend | fault_type | severity | confidence
0.85
0.92
0.97
0.995

## SO_Summary
SO_Summary — status & caveat (mirror EconomicAnalysis)
Skeleton: dengan data < min_days, run() emit 'insufficient_data' (INFO) dan SKIP SRR. Vocab fault: insufficient_data, insufficient_dependency, rdtools_error, soiling_detected, cleaning_recommended.
item | value
n_days_assumed
min_days_required
status
avg_daily_kwh
n_cleaning_recommended
SRR engine
note

## Raw_Data_MR
Raw_Data_MR — arus per-string 1 inverter (2 MPPT group) + POA
Model SUN2000-330KTL-H1 (WB03-10): MPPT1=[PV1-4], MPPT2=[PV5-9] — persis config/strings.yaml.
Arus konstan per string (sun di-faktorkan keluar; ratio invarian POA). PV9 glitch 3 langkah (baris 9-11).
timestamp | POA (W/m^2) | PV1 input current(A) | PV2 input current(A) | PV3 input current(A) | PV4 input current(A) | PV5 input current(A) | PV6 input current(A) | PV7 input current(A) | PV8 input current(A) | PV9 input current(A)
46156.5 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5035 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5069 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5104 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5139 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 3
46156.5174 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 3
46156.5208 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 3
46156.5243 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5278 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5312 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5347 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5382 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5417 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5451 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5486 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5521 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5556 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.559 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5625 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.566 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5694 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5729 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5764 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.5799 | 900 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.7569 | 120 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85
46156.7639 | 120 | 13 | 12.8 | 10.3 | 5.6 | 13 | 12.8 | 12.9 | 0 | 12.85

## Helpers_MR
Helpers_MR — daylight + median partner se-MPPT + ratio + qualifying + running-consec
daylight = (POA>cfg_mr_poa_threshold) & (POA>cfg_mr_poa_floor) [sub-gate POA saja; ephemeris di luar sheet].
median partner = MEDIAN(cell partner se-MPPT) -> meniru median(axis=1) atas sibling (mppt_ratio.py baris 274-276).
timestamp | POA | daylight | med_partner_PV1 | med_partner_PV2 | med_partner_PV3 | med_partner_PV4 | med_partner_PV5 | med_partner_PV6 | med_partner_PV7 | med_partner_PV8 | med_partner_PV9 | ratio_PV1 | ratio_PV2 | ratio_PV3 | ratio_PV4 | ratio_PV5 | ratio_PV6 | ratio_PV7 | ratio_PV8 | ratio_PV9 | qual_PV1 | qual_PV2 | qual_PV3 | qual_PV4 | qual_PV5 | qual_PV6 | qual_PV7 | qual_PV8 | qual_PV9 | consec_PV1 | consec_PV2 | consec_PV3 | consec_PV4 | consec_PV5 | consec_PV6 | consec_PV7 | consec_PV8 | consec_PV9

## M2b_MpptRatio
M2b_MpptRatio — keputusan per string (LIVE)
value = ratio_median_daylight ; emit bila max_consec >= cfg_mr_debounce_steps DAN bukan EMPTY.
severity: value<critical CRIT ¦ <high HIGH ¦ else MED. confidence = min(90,max(50,(1-value)*100)).
pv_string | mppt | partner_strings | ratio_median_daylight | max_consec | empty_by_design | emit | severity | confidence | status
PV1 | 1 | PV2, PV3, PV4 |  |  | 0
PV2 | 1 | PV1, PV3, PV4 |  |  | 0
PV3 | 1 | PV1, PV2, PV4 |  |  | 0
PV4 | 1 | PV1, PV2, PV3 |  |  | 0
PV5 | 2 | PV6, PV7, PV8, PV9 |  |  | 0
PV6 | 2 | PV5, PV7, PV8, PV9 |  |  | 0
PV7 | 2 | PV5, PV6, PV8, PV9 |  |  | 0
PV8 | 2 | PV5, PV6, PV7, PV9 |  |  | 0
PV9 | 2 | PV5, PV6, PV7, PV8 |  |  | 0

## M2b_MR_StringStatus
M2b_MR_StringStatus — replika artifact StringStatus (mppt_ratio.py baris 341-355)
Kolom = field artifact Python. ratio_event_median == ratio_median_daylight untuk fault sustained (M2_RE_11 §5.3).
poa_source | inverter_id | wb_id | pv_string | mppt | status | partner_strings | ratio_median_daylight | ratio_event_median | n_qualifying_steps | n_debounced_events | emitted_finding | daylight_samples
pyranometer_per_ws | WB05-INV05 | WB05 | PV1 | 1
pyranometer_per_ws | WB05-INV05 | WB05 | PV2 | 1
pyranometer_per_ws | WB05-INV05 | WB05 | PV3 | 1
pyranometer_per_ws | WB05-INV05 | WB05 | PV4 | 1
pyranometer_per_ws | WB05-INV05 | WB05 | PV5 | 2
pyranometer_per_ws | WB05-INV05 | WB05 | PV6 | 2
pyranometer_per_ws | WB05-INV05 | WB05 | PV7 | 2
pyranometer_per_ws | WB05-INV05 | WB05 | PV8 | 2
pyranometer_per_ws | WB05-INV05 | WB05 | PV9 | 2